## BoM
BM Global a.s.
C010-036-001-1 — Sohar 1 Power & Desalination Complex — Bill of Material
Customer: Suez-Tractebel Operation and Maintenance Oman LLC (STOMO) — Sohar Power Complex, Sultanate of Oman
Reference: Sohar 1 obsolescence assessment and DCS / server / field-component records
Issued: 23 June 2026 ¦ Prepared by: P. Roupec, Managing Director
Legend: BASE = included in baseline scope ¦ EMERGENCY = held against failure ¦ Recommended / Optional = to be quoted separately, subject to customer decision ¦ EXCLUDED = outside this scope. Prices follow in the commercial proposal.
Note: Quantities and part numbers from the Sohar 1 source data. 'Qty' is the installed quantity; spares to be held are noted in the comments.
Item | Area / System | Tag / ID | Function / Description | Qty | Model / Hardware | Quote | Licences needed / note | Scope | PO Status | Comments | Recommended Quantity | Comments
POS 10 — DCS Operator & Engineering Interface — OMLEX HMI Life Extension
1 | GT DCS | GT-OS-01..05 | GT Operator Working Station (OM 650, SCO-Unix) — replace with OMLEX MX | 5 | Celsius M420 → OMLEX MX | TBD | OMLEX (part of delivery) | BASE | TBD | 5 GT operator stations; existing displays/tags carried over | 6 | 3 in CCR , 3 in PCC - all with twin HMI screens. Currently we have only 5 OT linceses.
2 | BOP DCS | BOP-OS-01..07 | BOP Operator Working Station (OM 650) — replace with OMLEX MX | 7 | Celsius M420 → OMLEX MX | TBD | OMLEX (part of delivery) | BASE | TBD | 7 BOP operator stations | 2 | with twin HMI screens.
3 | GT DCS | GT-ES-01 | GT Engineering Working Station (ES 680, HP-Unix) | 1 | HP B2600 → OMLEX Eng. | TBD | OMLEX (part of delivery) | BASE | TBD | Display building / logic viewing | 1
4 | BOP DCS | BOP-ES-01 | BOP Engineering Working Station (ES 680, HP-Unix) | 1 | HP B2600 → OMLEX Eng. | TBD | OMLEX (part of delivery) | BASE | TBD |  | 1
5 | GT/BOP DCS | ES-SPARE-01 | Spare Engineering Working Station | 1 | HP B2600 → OMLEX Eng. | TBD | OMLEX (part of delivery) | BASE | TBD |  | 1
5A | HOPF clock | [6 empty] | BASE | TBD | Clock is to be upgraded and synchronised with both DCS networks.
|  |  | Additional info | [6 empty] | GT/BOP DCS - Backup/Restore - Backup/Restore procedures and tools are to be provided. GT DCS GT SU/Pus- KVM - must be equipped with KVM monitor
POS 15 — Servers, OPC & Programming Devices — Life Extension and Spares
6 | GT DCS | GT-SRV-A/B | GT Processing / Historian Server A & B (OM 650, SCO-Unix) | 2 | Celsius M420 | TBD | OMLEX / supported OS | BASE | TBD | Renew on current hardware | 2
7 | BOP DCS | BOP-PRC-A/B | BOP Processing Server A & B (OM 650) | 4 | Celsius M420 | TBD | OMLEX / supported OS | BASE | TBD | 4 units | 4
8 | BOP DCS | BOP-HST-A/B | BOP Historian Server A & B (OM 650) | 2 | Celsius M420 | TBD | OMLEX / supported OS | BASE | TBD |  | 2
9 | GT/BOP DCS | OPC-01 | OPC server & interface renewed (A16) — current supported OPC layer | 1 | Celsius M430 | TBD | OPC licence | BASE | TBD | Redundant OPC server quoted separately under C010-033; price carried in later | 1 | Two enquiries currently, only one should be processed.
10 | GT/BOP DCS | PG-01/02 | Simatic PG programming device (Windows 98) — AS620 / SIMADYN-D / S5 | 2 | PG 740 PIII | TBD | STEP5 / programming tools | BASE | TBD | PG2 currently not working | 2 | BM need to fix the issue on supplied PG /LAPTOP type
11 | GT/BOP DCS | SRV-SPARE-1..5 | Spare DCS servers — held against failure | 5 | Celsius M420 | TBD | — | EMERGENCY | TBD | Purchased and held by Customer at site; re-tested at maintenance visits | 2
12 | GT/BOP DCS | PRN-01..04 | ES 680 & DCS printers (GT + BOP) | 4 | HP M553 / M551 | TBD | — | BASE | TBD |  | 4
13 | GT DCS | WINTS-1/2/3 | WinTS performance servers (Windows Server 2003) | 3 | PS150-01979 | TBD | WinCC | Recommended | TBD | Performance monitoring / reports | 3
13a | GT | DOLPHIN | Dolphin data logger for WINTS | 3 | [6 empty] | 3 | Dolphin data loggers are to be and re-commissioned. Upgrade may be required if the current equipment is not working.
POS 20 — Stand-alone Operator Panels — OMLEX HMI Life Extension
14 | EDG | EDG-OP-01 | EDG operator panel | 1 | Siemens OP17 | TBD | — | BASE | TBD | EDG start / supervision | 1
15 | GT #1/2/3 | AI-OP-01/02/03 | Air-intake operator panel (GT #1 / #2 / #3) | 3 | Siemens OP7 | TBD | — | BASE | TBD | Air-intake alarms | 3
16 | PLC maint. | LAP-01/02 | Duct-burner / BOP PLC back-up laptop | 2 | Dell Inspiron / D610 | TBD | PLC tools | BASE | TBD | Program upload / download | 1
POS 25 — Data Archive Restoration — GT MOD / BOP VMOD
17 | BOP DCS | BOP-VMOD-01 | BOP DCS data archive server (not working) — replaced by new DELL server | 1 | Sunfire X4150 → new DELL server | TBD | Archive SW | BASE | TBD | New DELL server delivered; archiving restored | 1 | Is it possibel to share the hardware?
18 | GT DCS | GT-MOD-01/02 | GT DCS data archive drive (obsolete MOD) | 2 | Siemens / Sony MOD | TBD | — | BASE | TBD | Replaced by single supported historian | 1
POS 30 — Controller Spares — AS620 / SIMADYN-D / S5-95F / S5-95U
19 | GT | GT-SIMADYN | GT Controller (SIMADYN-D) | 3 sets | SIMADYN-D | TBD | — | BASE | TBD | Tested spare sets; GT start not possible on failure | 2 | check current stock and confirm
20 | GT | GT-AS620 | Simatic S5 Automation System (AS620) | 9 sets | SPPA-T2000 S5 | TBD | — | BASE | TBD |  | can we buy individual components | If both are same type of hardware, maintain a common pool. Can we use MSF controllers check current stock and confirm
21 | BOP | BOP-AS620 | Simatic S5 Automation System (AS620) | 13 sets | SPPA-T2000 S5 | TBD | — | BASE | TBD |  | can we buy individual components
22 | GT | GT-95F | Fail-safe protection controller | 3 sets | S5-95F | TBD | — | BASE | TBD | Safety controller | 1 set | check current stock and confirm
23 | GT | GT-95U | Argus valve controller | 3 sets | S5-95U | TBD | — | BASE | TBD |  | 1 set | check current stock and confirm
24 | BOP | BOP-CM104 | Third-party communication module | 6 | CM104 | TBD | — | BASE | TBD | LDC / OGC / Tariff / FMS / STG / 220 kV links | 2 | check current stock and confirm
25 | GT / BOP | CTRL-MIGR | Replacement to a current controller platform | — | — | TBD | — | Recommended | TBD | Deep obsolescence; future step, not priced here |  | Why is this not priced? If deep obsolescence, suppot/upgrade must be suggested.
POS 35 — Panel-mounted TXP / PLC Component Spares (installed component list)
26 | GT / BOP | 6ES5955-7NC12 | Power Supply | 50 | 6ES5955-7NC12 | TBD | SAP 806893 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 5 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
27 | GT / BOP | 6ES5308-3UC21 | Interface Module IM308 | 21 | 6ES5308-3UC21 | TBD | SAP 770815 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 2 | Stock list attached
28 | GT / BOP | 6ES5314-3UR11 | Interface Module IM314 | 12 | 6ES5314-3UR11 | TBD | SAP 770816/804262 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
29 | GT / BOP | 6GK1543-1AA01 | Communication Processor | 6 | 6GK1543-1AA01 | TBD | SAP 803126 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
30 | GT / BOP | 6ES5948-3UR23 | CPU 948R | 44 | 6ES5948-3UR23 | TBD | SAP 770838 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 4 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
31 | GT / BOP | 6ES5324-3UR11 | Interface Module IM324 | 22 | 6ES5324-3UR11 | TBD | SAP 770819/803416 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 2 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
32 | GT / BOP | 6GK1143-0TB01 | Communication Processor CP1430 | 44 | 6GK1143-0TB01 | TBD | SAP 770859 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 4 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
33 | GT / BOP | 6ES5304-3UB11 | Interface Module IM304 | 72 | 6ES5304-3UB11 | TBD | SAP 770814/804261 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 7 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
34 | GT / BOP | 6ES5482-UA20 | Monitoring Interface | 9 | 6ES5482-UA20 | TBD | SAP 770825/803422 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
35 | GT / BOP | 6ES530-3LA12 | Communication Processor | 6 | 6ES530-3LA12 | TBD | SAP 803420 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
36 | GT / BOP | 6ES7153-2AA02-0XB0 | Interface Module IM153-2 | 144 | 6ES7153-2AA02-0XB0 | TBD | SAP 803421 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 14 | Stock list attached
37 | GT / BOP | 6ES7323-1BL00-0AA0 | Digital Input/Output | 93 | 6ES7323-1BL00-0AA0 | TBD | SAP 770849 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 9 | Stock list attached
38 | GT / BOP | 6ES7331-7KF02-0AB0 | Analog Input | 63 | 6ES7331-7KF02-0AB0 | TBD | SAP 770850 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 6 | Stock list attached
39 | GT / BOP | 6ES5095-8FB01 | Automation System AG-95F | 12 | 6ES5095-8FB01 | TBD | SAP 770785 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
40 | GT / BOP | 6ES5482-8MA13 | Digital Input/Output | 39 | 6ES5482-8MA13 | TBD | SAP 803462 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 4 | Stock list attached
41 | GT / BOP | 6ES55431-8FA11 | Digital Input | 60 | 6ES55431-8FA11 | TBD | SAP 770823 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 6 | Stock list attached
42 | GT / BOP | 6ES5316-8FA12 | Interface Module IM 316 | 24 | 6ES5316-8FA12 | TBD | SAP 770817/804267 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 2 | Stock list attached
43 | GT / BOP | 6ES7321-1BL00-0AA0 | Digital Input 32CH | 18 | 6ES7321-1BL00-0AA0 | TBD | SAP 770847 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 2 | Stock list attached
44 | GT / BOP | 6ES7321-1BH02-0AA0 | Digital Input 16CH | 72 | 6ES7321-1BH02-0AA0 | TBD | SAP 770846 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 7 | Stock list attached
45 | GT / BOP | 6ES5450-8FA12 | Digital Output | 60 | 6ES5450-8FA12 | TBD | — | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 6 | Stock list attached
46 | GT / BOP | 6DD1600-0AK0 | CPU PM6 | 6 | 6DD1600-0AK0 | TBD | SAP 803408 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
47 | GT / BOP | 6DD1640-0AC0 | EM11 | 6 | 6DD1640-0AC0 | TBD | SAP 803409 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
48 | GT / BOP | 6DD1642-0BC0 | EA12 | 6 | 6DD1642-0BC0 | TBD | SAP 803410 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
49 | GT / BOP | 6DD1662-0AB0 | CS7 | 6 | 6DD1662-0AB0 | TBD | SAP 803412 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
50 | GT / BOP | 6DD1688-0AE2 | SS52 | 6 | 6DD1688-0AE2 | TBD | SAP 803414 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
51 | GT / BOP | 6DD1661-0AB1 | CSH11 | 6 | 6DD1661-0AB1 | TBD | SAP 803411 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
52 | GT / BOP | 6DD1660-0BA0 | CS12 | 3 | 6DD1660-0BA0 | TBD | SAP 803413 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
53 | GT / BOP | 6DD1660-0B00 | CS22 | 3 | 6DD1660-0B00 | TBD | SAP 803419 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
54 | GT / BOP | 6DL3100-8AA | Input/Output Module ADD7-FEM | 12 | 6DL3100-8AA | TBD | SAP 701390 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
55 | GT / BOP | 6ES5318-8MB13 | Interface Module | 3 | 6ES5318-8MB13 | TBD | — | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
56 | GT / BOP | 6ES5265-8MA01 | High Speed Subcontrol | 6 | 6ES5265-8MA01 | TBD | SAP 803461 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
57 | GT / BOP | 6ES7331-7PF10-0AB0 | 8xTC, 1xPT100 | 21 | 6ES7331-7PF10-0AB0 | TBD | SAP 806776 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 2 | Stock list attached
58 | GT / BOP | 6ES7331-7SF00-0AB0 | Analog Input (Ex) | 51 | 6ES7331-7SF00-0AB0 | TBD | SAP 770851 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 5 | Stock list attached
59 | GT / BOP | 6ES7322-1BH01-0AA0 | Digital Output | 3 | 6ES7322-1BH01-0AA0 | TBD | SAP 770848 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
60 | GT / BOP | 6ES5095-8MB04 | Compact Unit S5-95U | 6 | 6ES5095-8MB04 | TBD | SAP 701395 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
61 | GT / BOP | 6ES7332-5HD01-0AB0 | Digital Input/Output | 3 | 6ES7332-5HD01-0AB0 | TBD | — | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
62 | GT / BOP | — | CM 104 | 6 | — | TBD | SAP 803426 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
63 | GT / BOP | 6DP1280-8AB | FUM 280 | 66 | 6DP1280-8AB | TBD | SAP 803406 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 7 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
64 | GT / BOP | 6DP1230-8CC | FUM 230 | 194 | 6DP1230-8CC | TBD | SAP 700833/803405 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 19 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
65 | GT / BOP | 6DP1210-8BC | FUM 210 GB & FUM 210 ESG | 334 | 6DP1210-8BC | TBD | SAP 700834/803404 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 33 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
66 | GT / BOP | 6DP1614-8BB | IM 614 | 102 | 6DP1614-8BB | TBD | SAP 803427 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 10 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
67 | GT / BOP | 6DP1511-8AA | FUM 511 | 15 | 6DP1511-8AA | TBD | SAP 700831/803407 | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 2 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
68 | GT / BOP | — | DI/DO Monitoring Module S5-DEDA | 13 | — | TBD | — | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached, Qty in column ''F'' is to be reduced as MSF is no more in service.
69 | GT / BOP | 6DD1683-0CC0 Rev B | Power Supply 8P22 (SIMADYN racks) | 6 | 6DD1683-0CC0 Rev B | TBD | — | BASE | TBD | Customer purchases and holds 2 of each selected item at site; re-tested at visits | 1 | Stock list attached
POS 40 — Ancillary Systems (Optional)
70 | GT / PCC / CCR | FF-PANEL | Fire-fighting system panels | 4 sets | MINIMAX | TBD | — | Optional | TBD |  |  | Not part of the current scope
71 | IA Comp. | IA-CTRL | Instrument-air compressor controller | 3 sets | IR Intellisys | TBD | — | Optional | TBD |  | 1 | BM Global may offer this part
72 | Drinking water | DW-CTRL | Drinking-water system controller | 1 set | Grundfos PMU+PFU 2000 | TBD | — | Optional | TBD |  | 1 set | BM Global may offer this part
73 | Security | CCTV-DVR | CCTV DVR | 1 | DVR | TBD | — | Optional | TBD |  |  | Not part of the current scope
74 | Gas station | GC-01 | Gas chromatograph | 1 set | Daniel 500 / 2350A | TBD | — | Optional | TBD | Gas quality / flow metering |  | Not part of the current scope
75 | Fire pump | FF-DIESEL | FF diesel-engine control panel | 1 set | Teledyne / MINIMAX | TBD | — | Optional | TBD |  |  | Not part of the current scope
76 | Field | TEL-01..39 | Weatherproof analog telephone, IP66 | 39 | Telenet | TBD | — | Optional | TBD |  |  | Not part of the current scope
77 | Telephony | EPABX-01 | EPABX server | 1 | IBM S8500B | TBD | — | Optional | TBD |  |  | Not part of the current scope
POS 80 — Structured Support & On-Call Assistance
78 | Support | SUP-80 | On-call remote support for the delivered scope; spares inventory held by the Customer at site | 1 | — | TBD | — | BASE | TBD | Customer holds spares at site; re-tested at visits | 1 | Unit rate is to be quoted.
POS 85 — Half-Yearly Maintenance Site Visit
79 | Support | SUP-85 | Scheduled on-site maintenance — twice per year; visit record after each visit | 2 | — | TBD | — | BASE | TBD | Per year | 4 | One visit in summer - GT + BOP Three visits in winter during the time of annual maitenance of respective GT. During one such visit, the BOP PM services are also to be performe.
POS 90 — Support — Year 2 onward
80 | Support | SUP-90 | Continuation of POS 80 + POS 85 in subsequent years | 1 | — | TBD | — | BASE | TBD | Per year, for the agreed support period | 1 | Please quote
POS 50 — Network Renewal & Isolation (managed switches + data diodes) — placeholder quantities, to be confirmed
81 | GT DCS — plant bus | GT-SW-PB-01..04 | GT plant-bus ring switch (managed, redundant ring) | 4 | FS IES3100-16TM | TBD | — | BASE | TBD | FS industrial managed switch — economical, comparable to Hirschmann, readily available; suitable for the 9-year life extension | 4 | Total No of OSM=43 (GT-15, BOP-28)
82 | GT DCS — terminal bus | GT-SW-TB-01..04 | GT terminal-bus ring switch (managed, redundant ring) | 4 | FS IES3100-16TM | TBD | — | BASE | TBD | FS industrial managed switch — economical, comparable to Hirschmann, readily available; suitable for the 9-year life extension | 4
83 | BOP DCS — plant bus | BOP-SW-PB-01..04 | BOP plant-bus ring switch (managed, redundant ring) | 4 | FS IES3100-16TM | TBD | — | BASE | TBD | FS industrial managed switch — economical, comparable to Hirschmann, readily available; suitable for the 9-year life extension | 4
84 | BOP DCS — terminal bus | BOP-SW-TB-01..04 | BOP terminal-bus ring switch (managed, redundant ring) | 4 | FS IES3100-16TM | TBD | — | BASE | TBD | FS industrial managed switch — economical, comparable to Hirschmann, readily available; suitable for the 9-year life extension | 4
85 | Network boundary | DD-01/02 | Data diode — control-network isolation from external connections | 2 | Data diode | TBD | — | BASE | TBD | One-way isolation; quantity to be confirmed | 2
86 | GT/BOP DCS | SFP-SPARE | SFP uplink modules / patch leads (switch interconnect) | TBD | FS SFP | TBD | — | Recommended | TBD | Uplink optics for ring interconnect; quantity to be confirmed